| Date : 30/04/2021 Page 1 of 3 | Technical Specification Eccentric Plug (Ball) Valves |  |
| --- | --- | --- |

1. SCOPE

This specification sets the minimum acceptable requirements for supply of eccentric plug valve type for size range of DN100 – DN1800.

2. APPLICABLE STANDARDS

| ISO5752 | Face to face dimensions of valves |
| --- | --- |
| ISO 7005 | Metallic flanges |
| EN 1074-1 | Valves for water supply – Part 1: Fitness for purpose req. and Appropriate verification tests (General Req.) |
| EN 1074-2 | Valves for water supply – Part 2: Fitness for purpose req. and Appropriate verification tests (Isolating valves.) |
| ISO 5211 | Actuator Mounting Flange. |
| ISO5208 BSEN12266 | Industrial valves, Pressure testing of metallic valves |
| EN 1092 | Flanges and their joints – Part 2: Cast Iron flanges, Circular flanges for pipes, valves, fittings and accessories, PN designated |
| EN 1563 | Spheroidal graphite cast iron |

3. CONSTRUCTION REQUIREMENTS

Valves shall be of the eccentric resilient seated plug/ball valves which are suitable for sewage, slurry, wastewater, waterworks and raw water and applications. Face-to-face dimensions shall in accordance with ISO 5752. Nominal pressure rating as per design requirement (Max PN16 bars)

The valves shall have flanged connections, with the flanges drilled in accordance with the ISO 7005 and EN 1092-2 standards and pressure ratings shall be as per project requirement.

Valve ports shall be of round port type. The body seat shall be furnished with a welded-in overlay stainless steel seat, precisely machined inside the valve body for providing high corrosion and wear resistance, long service life and reliability.

| Date : 30/04/2021 Page 2 of 3 | Technical Specification Eccentric Plug (Ball) Valves |  |
| --- | --- | --- |

The plug/ball shall be of eccentric design, and shall be designed to withstand three time of the rating pressure of the valve. The plug/ball shall be contoured to ensure the lowest possible resistance to flow. Plug/ball shall have an adjustable and removable resilient seal for easy re-adjustment or replacement. The disc rubber seal shall be of one piece moulded construction and secured in its place by means of a retaining ring that is fixed to the disc by means of stainless steel fasteners. Valve design shall allow the replacement of disc seal without removing the valve from pipeline. The disc seat shall be upward when the valve is open.

The eccentric design shall allow the seal lifted-off the body seat after short travel (about 5°). There is a large gap area between ball and body which is flushed the flow in intermediate position about the self -cleaning effect

Shafts shall be of Stainless Steel, designed to withstand the maximum torque that will be imposed by the operator. It shall have two Shafts one drive shaft and one stub shaft designed to transmit required torques and withstand stresses imposed under severe operating conditions. Plug/ball valve shall be furnished with self-lubricating bearing sleeve type. Shaft seals shall be a gland type with O-Ring or U-Cup Type

Worm gear shall be of fully enclosed type and shall require a maximum input force on the hand wheel of not more than 356N pull to develop the required torque for rated working pressure. The worm gear box shall be furnished with a device to indicate the valve position. The gearbox shall be self-locking type. The gear box shall have end stops in both directions for rotation of minimum 90°. The mounting flange of the worm gearbox to the valve shall be according to ISO 5211. The maximum output torque of the GB shall be greater than the valve unseating torque by a min. of 20%.

For electrically actuated valves, gearbox shall have suitable adaption for electric actuator of suitable size. Torque of electric actuator shall be higher 20% than the valve required torque at any position of the valve.

Valves shall be provided with internal and external coating of non-toxic epoxy with a minimum dry film thickness of 250 microns at any point. The coating shall be done after shot blasting in accordance with ISO 8501-01 Gr. SA. 2.5.

| Date : 30/04/2021 Page 3 of 3 | Technical Specification Eccentric Plug (Ball) Valves |  |
| --- | --- | --- |

Hydrostatic testing (Body test, seat test) shall be performed in each valve in accordance with ISO 5208 Or BS EN 12266-1. Valves shall show no signs of visible leakage during testing.

Marking shall be cast on the body with raised letters or engraved on a separate stainless steel name plate and it Shall indicates the nominal valve size, manufacturer’s name, design pressure rating and the year of manufacture.

4. Material Specifications

| Body | Ductile Iron EN 400/12 or Ductile Iron EN 500/7 acc. To EN1563 |
| --- | --- |
| Plug | Ductile Iron EN 400/12 or Ductile Iron EN 500/7 acc. To EN1563 |
| Cover | Ductile Iron EN 400/12 or Ductile Iron EN 500/7 acc. To EN1563 |
| Retaining ring | Ductile Iron EN 400/12 or Ductile Iron EN 500/7 acc. To EN1563 |
| Gland | Ductile Iron EN 400/12 or Ductile Iron EN 500/7 acc. To EN1563 |
| Body Seat | Welded overlay SS316 |
| Plug Seal | NBR Rubber |
| Driving /stub Shafts | X20Cr13 (AISI 420) |
| Retaining ring bolts | SS316 |
| Bearing | Self-Lubricating Bearing |
| Seals | NBR Rubber |
| Cover bolts | Galvanized steel Gr8.8 |