| Date : 30/04/2021 Page 1 of 3 | Technical Specification Swing Flex Check Valves |  |
| --- | --- | --- |

1. SCOPE

This specification sets the minimum acceptable requirements for supply swing flex check valve types for size range of DN65 – DN1000.

2. APPLICABLE STANDARDS

| BS EN 558-1 | Industrial valves face to face and center to face dimensions of metal valves for use in flanged pipes systems |
| --- | --- |
| ISO5752 | Face to face dimensions of valves |
| DIN3232 | Industrial valves and their dimensions |
| BS5153 | Cast iron check valves for general purposes |
| EN 1074-1 | Valves for water supply – Part 1: Fitness for purpose req. and Appropriate verification tests (General Req.) |
| EN 1074-3 | Valves for water supply – Fitness for purpose requirements and appropriate verification tests Part 3: Check valves |
| EN 12266-1 | Testing of valves Part 1: Pressure tests, test procedures and acceptable criteria - Mandatory requirements – (Industrial valves) |
| ISO 7005 | Metallic flanges |
| ISO5208 | Industrial valves, Pressure testing of metallic valves |
| EN 1092 | Flanges and their joints – Part 2: Cast Iron flanges, Circular flanges for pipes, valves, fittings and accessories, PN designated |
| EN1563 | Spheroidal graphite cast iron |

3. CONSTRUCTION REQUIREMENTS

Valves shall be of rubber flapper (swing flex) check valve types suitable for sewage, wastewater, raw water and slurry applications. The check valve shall be of the full flow body type, the valve shall be of the elastomeric flexible disc type and the disc is the only moving part that shall assures long life with minimal maintenance. The valve shall have no packing, shafts, arms, mechanical hinges, pivot pins or bearings to wear out.

Valves face to face dimension of valves shall comply with ISO 5752 Series 10 for valves up to DN600 and with DIN3232 for size from DN700 - DN1000. Valves shall have a nominal pressure rating as per design requirement (Max. PN16 bars).

| Date : 30/04/2021 Page 2 of 3 | Technical Specification Swing Flex Check Valves |  |
| --- | --- | --- |

The valves shall have flanged connections with the flanges drilled in accordance with the ISO 7005 and EN 1092-2 standards and pressure ratings shall be as per project requirement.

The valve body design shall be full flow type that equal to nominal pipe diameter at all points through the valve. The seating surface shall be on a 45° degrees angle to minimize disc travel. Disc only moves 35 degrees to reach its full opening/closing position. The valve design shall allowing removal of the disc without removing the valve from the line. The valve cover shall be domed in shape to provide flushing action over the disc for operating in lines containing high solids content. The valve shall be installed in horizontal or vertical position.

The disc shall be of one-piece construction (Precision molded), fully encapsulated with nylon reinforced rubber to prevent corrosion and provided uninterrupted service. Disc shall have an integral O-ring sealing surface. The disc shall have a rubber flexible portion that ensures the flex-action of disc during opening/closing cycles. The flexible portion of the disc shall be reinforced with nylon threading for strengthening.

Non-Slam closing characteristics shall be provided through a short 35 degree disc stroke and an elastomeric flexible disc return action. Disc provides a cracking pressure of 0.25 psig. The valve disc shall remain drop tight shut-off at both high and low pressures up to 0.5bars

Valves shall be equipped with hydraulic dampers (internal type), which slows down the closure to avoid sudden slamming of the valve disc. The adjustable speed dashpot slows down the closing of the disc in order to prevent water hammer. The valve closing speed can be adjusted by change the flow control throttling valve on hydraulic damper. Hydraulic damper controls the last 10% of the valve closure to reduce water hammer.

Valves shall be provided with internal and external coating of non-toxic fusion bonded epoxy (powder coating) with a minimum dry film thickness of 250 microns at any point. The coating shall be done after shot blasting in accordance with ISO 8501-01 Gr. SA. 2.5.

Hydrostatic testing (Body test, seat test) shall be performed in each valve in accordance with ISO 5208 Or EN 12266-1. Valves shall show no signs of visible leakage during testing.

| Date : 30/04/2021 Page 1 of 3 | Technical Specification Swing Flex Check Valves |  |
| --- | --- | --- |

Marking shall be cast on the body with raised letters or engraved on a separate stainless steel name plate and it may indicates the nominal valve size, manufacturer’s name, design pressure rating and the year of manufacture.

Valves shall be supplied with forged steel lifting eyes to ensure secure handling of the valve during transportation and installation.

4. Material Specifications

| Body | Ductile Iron EN-GJS-400/12 or Ductile Iron EN-GJS-500/7 acc. To EN1563 |
| --- | --- |
| Cover | Ductile Iron EN-GJS-400/12 or Ductile Iron EN-GJS-500/7 acc. To EN1563 |
| Disc | Alloy steel fully vulcanized with NBR rubber |
| Cover seals | EPDM (NBR) |
| Bolts | Galvanized steel GR8.8 |