| Date : 30/04/2021 Page 1 of 3 | Technical Specification Wastewater air valves |  |
| --- | --- | --- |

1. SCOPE

This specification sets the minimum acceptable requirements for supply water air valve types for size range of DN80 – DN200.

2. APPLICABLE STANDARDS

| EN 1074-1 | Valves for water supply – Part 1: Fitness for purpose req. and Appropriate verification tests (General Req.) |
| --- | --- |
| EN 1074-4 | Valves for water supply – Fitness for purpose requirements and appropriate verification tests - Air valves |
| EN 12266-1 | Testing of valves Part 1: Pressure tests, test procedures and acceptable criteria - Mandatory requirements – (Industrial valves) |
| ISO 7005 | Metallic flanges |
| ISO5208 | Industrial valves, Pressure testing of metallic valves |
| EN 1092 | Flanges and their joints – Part 2: Cast Iron flanges, Circular flanges for pipes, valves, fittings and accessories, PN designated |
| EN1563 | Spheroidal graphite cast iron |

3. CONSTRUCTION REQUIREMENTS

Valves shall be of single chamber designed to prevent dynamic closure under higher air velocity. Valves shall be manufactured and tested in accordance to BSEN1074-1&4.

Valves shall be suitable for sewage, wastewater, municipal Water, irrigation pipeline mains, distribution networks, pumping stations and water treatment plants. Valves pressure rating shall be PN10, PN16.

The valves shall have flanged connections with the flanges drilled in accordance with the ISO 7005 and EN 1092-2 standards and pressure ratings shall be as per project requirement.

| Date : 30/04/2021 Page 2 of 3 | Technical Specification Wastewater air valves |  |
| --- | --- | --- |

Valves shall be of single chamber double orifice three functions combination air valves and automatic float operated. The three function of the valve shall include: (1) Valves may exhaust large quantities of air during the filling of a piping system and close upon liquid entry. (2) Valve shall open during draining or if a negative pressure occurs. And (3) valve shall also release accumulated air from a piping system while the system is in operation and under pressure.

Valves shall be of large lower body designed with strongly sloped funnel shaped walls to avoid deposit of grease or other material (The conical body shaped body shall maintain the maximum distance between the liquid and the sealing mechanism to prevent valve blocking.). Valve body shall containing four cast ribs to guide the stainless steel float. Upper body shall contain a guide casing that protects the air release device against fluttering during rapid filling.  Large stainless steel float, placed on the lower body, and connected through a stainless steel rod to the air release system. The float guided in two points to ensure the maximum accuracy.

The valve shall be designed to allow perfect operation - without blocking - in raw sewage, wastewater, and in high solids applications. Floats shall be unconditionally guaranteed against failure including pressure surges. A resilient buffer shall be provided to cushion the float during sudden opening conditions. The seat shall provide drop tight shut off to the full valve pressure rating.

Valve operating mechanism shall be of stainless steel float, placed on the lower body and connected through a stainless steel rod to the air release system. The valve shall have a ball valve that can be opened to release trapped pressure and drain the valve body prior to maintenance and for back-flushing – washing out - during maintenance.

Valves shall be provided with internal and external coating of non-toxic fusion bonded epoxy (powder coating) with a minimum dry film thickness of 250 microns at any point. The coating shall be done after shot blasting in accordance with ISO 8501-01 Gr. SA. 2.5.

Hydrostatic testing (Body test, seat test) shall be performed in each valve in accordance with ISO 5208 Or EN 12266-1. Valves shall show no signs of visible leakage during testing.

Marking shall be cast on the body with raised letters or engraved on a separate stainless steel name plate and it may indicates the nominal valve size, manufacturer’s name, design pressure rating and the year of manufacture.

| Date : 30/04/2021 Page 3 of 3 | Technical Specification Wastewater air valves |  |
| --- | --- | --- |

4. Material Specifications

| Body - Middle Part - Seat cover - Cover | Ductile Iron EN-GJS-400/12 or Ductile Iron EN-GJS-500/7 acc. To EN1563 |
| --- | --- |
| Float -Stem -Cage -Sealing Arc | SS3316 |
| Small orifice seat, Large orifice seat | NBR rubber |
| Disc seat | NBR rubber |
| Bolts, Studs, and nuts | SS316 |